## Electrical
ELECTRICAL METERS
Meter No. | Description | Switch Board | Tenant | Location | Meter Type | Network | Address | Status | Notes
EMS Gateway No1 - LG room with switches IP: 172.17.25.100
Life Safety Room Main I/C Fire Services - Far end | ML2-V1-FPS | Life Safety | Landlord | LV Room | Carlo Gavzzi EM26-96 | RS485, Modbus | 23 | Complete
HV/LV Room Main I/C T1 | ML2-V1-ICT1 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM26-96 | RS485, Modbus | 11 | Complete
HV/LV Room Main I/C T2 | ML2-V1-ICT2 | SWB 2 | Landlord | LV Room | Carlo Gavzzi EM26-96 | RS485, Modbus | 12 | Complete
HV/LV Room Chiller 1 WCA/1B/001 | ML2-V1-CHILLER1 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 13 | Complete
HV/LV Room Chiller 2 WCA/1B/002 | ML2-V1-CHILLER2 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 14 | Complete
HV/LV Room AHU No1 PPC/1B/R/007A | ML2-V2-PPC1 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 15 | Complete
HV/LV Room PPC/ 1B/R/010 Chilled Water Pumps | ML2-V2-PPC2 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 16 | Complete
HV/LV Room Chiller 3 WCA/1B/003 | ML2-V1-CHILLER3 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 17 | Complete
HV/LV Room AHU No2 PPC/1B/R/006 | ML2-V2-PPC3 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 18 | Complete
HV/LV Room Chiller 4 WCA/1B/004 | ML2-V1-CHILLER4 | SWB 1 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 19 | Complete
AHU No 2 PPC/1B/R/006A | ML2-V1-AHU02 | SWB 2 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 20 | Complete
AHU No1 PPC/1B/R/007 | ML2-V1-AHU01 | SWB 2 | Landlord | LV Room | Carlo Gavzzi EM21 | RS485, Modbus | 21 | Complete
Top of Tenants Riser B2 Room | ML2-V1-TNTRSR | N/A | Landlord | Roof Room B02 | Carlo Gavzzi EM21 | RS485, Modbus | 22 | Complete
ML2-V1-ShowerBLK |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 1 | Complete
ML2-V1-DBL9B1 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 2 | Complete
ML2-V1-DBL6B1 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 3 | Complete
ML2-V1-DBL3B1 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 4 | Complete
ML2-V1-DBL1GB1 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 5 | Complete
ML2-V1-PPC1BLG002 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 6 | Complete
ML2-V1-DB1L/LG |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 7 | Complete
ML2-V1-DBL6B2 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 8 | Complete
ML2-V1-PPC1BR008 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 9 | Complete
ML2-V1-PPC1BR009 |  | SWB 1 | Landlord | Roof EMS Panel | Carlo Gavzzi EM21 | RS485, Modbus | 10 | Complete
EMS Gateway No1 - LG room with switches IP: 172.17.25.101
DB/8LP Total |  | n/a | Tenant | Level 8 | Schneider IEM3225 | RS485, Modbus | 30 | Complete
DB/8LP Top |  | n/a | Tenant | Level 8 | Schneider IEM3225 | RS485, Modbus | 31 | Complete
DB/8M Power |  | n/a | Tenant | Level 8 | Schneider IEM3225 | RS485, Modbus | 29 | Complete
Level 8 Power No1 | ML2-V2-8TH-1 | n/a | Tenant | Level 8 | Carlo Gavzzi EM21 | RS485, Modbus | 26 | Complete
Level 8 Lighting No2 | ML2-V2-8TH-2 | n/a | Tenant | Level 8 | Carlo Gavzzi EM21 | RS485, Modbus | 27 | Complete
Level 8 Comms No3 | ML2-V2-8TH-3 | n/a | Tenant | Level 8 | Carlo Gavzzi EM21 | RS485, Modbus | 28 | Complete
Level 7 Lighting | ML2-V2-7TH-1 | n/a | Tenant | Level 7 | Carlo Gavzzi EM21 | RS485, Modbus | 23 | Complete
Level 7 Power | ML2-V2-7TH-2 | n/a | Tenant | Level 7 | Carlo Gavzzi EM21 | RS485, Modbus | 24 | Complete
Level 7 UPS Board | ML2-V2-7TH-3 | n/a | Tenant | Level 7 | Carlo Gavzzi EM21 | RS485, Modbus | 25 | Complete | 2
DB6/TM |  | n/a | Tenant | Level 6 | Schneider IEM3225 | RS485, Modbus | 11 | Complete | 3
DB6/TPL Total |  | n/a | Tenant | Level 6 | Schneider IEM3225 | RS485, Modbus | 13 | Complete
DB6/TPL Top |  | n/a | Tenant | Level 6 | Schneider IEM3225 | RS485, Modbus | 12 | Complete
DB5/TM |  | n/a | Tenant | Level 5 | Schneider IEM3225 | RS485, Modbus | 8 | Complete
DB5/TPL Total |  | n/a | Tenant | Level 5 | Schneider IEM3225 | RS485, Modbus | 10 | Complete
DB5/TPL Top |  | n/a | Tenant | Level 5 | Schneider IEM3225 | RS485, Modbus | 9 | Complete
DB4/TLM |  | n/a | Tenant | Level 4 | Schneider IEM3225 | RS485, Modbus | 16 | Complete
DB4 TP Total |  | n/a | Tenant | Level 4 | Schneider IEM3225 | RS485, Modbus | 15 | Complete
DB4 Top Section |  | n/a | Tenant | Level 4 | Schneider IEM3225 | RS485, Modbus | 14 | Complete
DB3/TLM Top |  | n/a | Tenant | Level 3 | Schneider IEM3225 | RS485, Modbus | 6 | Complete
DB3/TLM Total |  | n/a | Tenant | Level 3 | Schneider IEM3225 | RS485, Modbus | 7 | Complete
DBT/L+P/02 Total |  | n/a | Tenant | Level 2 | Schneider IEM3225 | RS485, Modbus | 3 | Complete
DBT/L+P/02 Top |  | n/a | Tenant | Level 2 | Schneider IEM3225 | RS485, Modbus | 2 | Complete
Level 2 NE/1 | ML2-V2-2ND-1 | N/A | Tenant | Level 2 | Carlo Gavazzi EM21 | RS485, Modbus | 36 | Complete
Level 2 PB2 | ML2-V2-2ND-2 | N/A | Tenant | Level 2 | Carlo Gavazzi EM21 | RS485, Modbus | 35 | Complete
DBT/L+P/01 Total |  | N/A | Tenant | Level 1 | Schneider IEM3225 | RS485, Modbus | 32 | Complete
DBT/L+P/01 Top |  | N/A | Tenant | Level 1 | Schneider IEM3225 | RS485, Modbus | 40 | Complete
Level 1 T3 top - GPL & FCU's - C Gavazzi EM24DIN | ML2-V2-1ST-2 | N/A | Tenant | Level 1 | Carlo Gavazzi EM21 | RS485, Modbus | 33 | Complete
Level 1 T2 LH - GPL & FCU's - C Gavazzi EM24DIN | ML2-V2-1ST-1 | N/A | Tenant | Level 1 | Carlo Gavazzi EM21 | RS485, Modbus | 34 | Complete
Level 1 T4 RH - GPL & FCU's - C Gavazzi EM24DIN | ML2-V21-ST-3 | N/A | Tenant | Level 1 | Carlo Gavazzi EM21 | RS485, Modbus | 37 | Complete | 4
Notes
2. No power on phase 1. Further investigation required
3. Negative power on phase 1. Possible CT installed incorectly
4. Negative power on all 3 phases.

## Gas
GAS METERS
Meter No. | Serving | Location | Serial No. | Meter Type | Communications | Network | Scaling | Status | Notes
143/04/M/G/03 | Retail Corridoor Dim-T Restaurant Gas Submeter (High Level) | LG | M025K0039810D6 |  | Pulse | TBD | 1p/m3 | In Progress
143/04/M/G/02 | Retail Corridoor Strada Restaurant Gas Submeter (High Level) | LG | 40019515 |  | Pulse | TBD | 1p/m3 | In Progress
143/04/M/G/01 | Main Bldg gas meter | LG | M0310 D1855 01B7 | Roots Master Series B4 | Pulse | BMS | 1p/m3 | Complete
143/04/M/G/04 | Gas Room Gaucho | LG | P-34365/2010 | Quantometer CPT-01 | Pulse | BMS | 1p/m3 | Complete
143/04/M/G/05 | Gas Room Boilers Meter | LG | P-23308/2009 | Quantometer CPT-01 | Pulse | BMS | 1p/m3 | Complete
Notes

## Water
WATER METERS
Meter No. | Serving | Location | Serial No. | Meter Type | Communications | Network | Scaling | Status | Notes
143/04/M/W/07 | Gaucho - Mezz (Inside resturant) | Mezanine (Gauchos) |  |  | n/a | n/a | n/a | In Progress | 1
G24 | Water Tank Room | Water Tank Room | 412007298 | Crodonel DN100 | Pulse | TBD | TBD | In Progress
143/04/M/W/06 | Gaucho - Grd (Inside resturant) | Ground (Gauchos) |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/03 | Retail Corridor Strada Restaurant Water Submeter (Hign Level) | Ground (Retail Cooridor Strada) |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/05 | Retail Corridoor Dim-T Restaurant Water Submeter (High Level) | Ground (Retail Cooridor Dim-T) |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/01 | Sprinkler Valve RoomMain 100 mm | Ground |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/02 | Sprinkler Valve Room Bypass | Ground |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/04 | Water Submeter Gym | Basement |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/08 | Sprinkler Valve Room Retail - 37Degrees / Strada / Dim-T / Gaucho | Basement |  |  | n/a | n/a | n/a | In Progress | 1
143/04/M/W/09 | Sprinkler Valve Room External - External Taps | Basement |  |  | n/a | n/a | n/a | In Progress | 1
Notes
1 | No pulse facility available. Meters needs replacing